{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":8,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","3MXS-K"]
[]
[]
[]
[]
["","","","","","3MXS40K3V1B","3MXS40K3V1B2","3MXS40K2V1B"]
["Уровень звукового давления","Hагрев","","Ном.","дБ(A)","47","47"]
["","Охлаждение","","Ном.","дБ(A)","46","46"]
["Стандартные аксессуары","Инструкции по установке","","","","1","1"]
["","Сливная пробка","","","","1","1"]
["Хладагент","Charge","","","TCO2Eq","4.2","4.2"]
["","ПГП","","","","2,087.5","2,087.5"]
["","Заправка","","","кг","2.0","2.0"]
["","Тип","","","","R-410A","R-410A"]
["Подсоединения труб","Перепад уровней","IU - IU","Макс.","м","7.5","7.5"]
["","","IU - OU","Макс.","м","15","15"]
["","Дополнительная заправка хладагента","","","кг/м","0,02 (для длины труб свыше 30 м)","0,02 (для длины труб свыше 30 м)"]
["","Общая длина трубопроводов","Система","Фактическая","м","50","50"]
["Компрессор","Тип","","","","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа"]
["Размеры","Блок","","Ширина","мм","936","936"]
["","","","Глубина","мм","300","300"]
["","","","Высота","мм","735","735"]
["Масса","Блок","","","кг","49","49"]
["Power supply","Фаза","","","","1~","1~"]
["","Частота","","","Гц","50","50"]
["","Напряжение","","","V","230","230"]
["Примечания","","","","","(1) - Содержит фторированные парниковые газы","(1) - Содержит фторированные парниковые газы"]
["Размеры","Блок","","Размеры-=-Блок-=-Высота-=-мм","мм","","","735"]
["","","","Ширина","мм","","","936"]
["","","","Глубина","мм","","","300"]
["Масса","Блок","","","кг","","","49"]
["Компрессор","Тип","","","","","","Герметичный компрессор ротационного типа"]
["Рабочий диапазон","Охлаждение","Темп. нар. возд.","Мин.","°C сух.т.","","","-10"]
["","","","Макс.","°C сух.т.","","","46"]
["","Hагрев","Темп. нар. возд.","Мин.","°CWB","","","-15"]
["","","","Макс.","°CWB","","","15.5"]
["Уровень звукового давления","Охлаждение","","Уровень звукового давления-=-Охлаждение-=-Ном.-=-дБ(A)","дБ(A)","","","46"]
["","Hагрев","","Уровень звукового давления-=-Hагрев-=-Ном.-=-дБ(A)","дБ(A)","","","47"]
["Хладагент","Тип","","","","","","R-410A"]
["","Заправка","","","кг","","","2.0"]
["","Заправка","","","tCO2Eq","","","4.2"]
["","ПГП","","","","","","2087.5"]
["Подсоединение труб","Длина трубы","Макс.","НБ - ВБ","м","","","50"]
["Подсоединения труб","Дополнительная заправка хладагента","","","кг/м","","","0,02 (для длины труб свыше 30 м)"]
["","перепад уровня","IU - OU","Макс.","м","","","15"]
["","","IU - IU","Макс.","м","","","7.5"]
["Стандартные аксессуары","Installation manual","","","","","","1"]
["","Drain plug","","","","","","1"]
["Электропитание","Фаза","","","","","","1~"]
["","Частота","","","Гц","","","50"]
["","Напряжение","","","V","","","230"]