{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":39,"n_cols":12,"rows_kept":39,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXM-A"]
[]
[]
[]
[]
["","","","","","RXM20A5V1B","RXM25A5V1B","RXM35A5V1B","RXM42A5V1B","RXM50A5V1B","RXM60A5V1B","RXM71A5V1B"]
["Размеры","Блок","","Размеры-=-Блок-=-Высота-=-мм","мм","610","610","610","610","734","734","734"]
["","","","Ширина","мм","923","923","923","923","954","954","954"]
["","","","Глубина","мм","367","367","367","367","401","401","401"]
["Масса","Блок","","","кг","36","36","36","40","49","49","55"]
["Двигатель вентилятора","Скорость","Охлаждение","Самый низкий","об/мин","600","600","600","600","500"]
["Компрессор","Тип","","","","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа","Герметичный компрессор ротационного типа"]
["Рабочий диапазон","Охлаждение","Темп. нар. возд.","Мин.","°C сух.т.","-10","-10","-10","-10","-10","-10","-10"]
["","","","Макс.","°C сух.т.","50","50","50","50","50 (1)","50","46"]
["","Hагрев","Темп. нар. возд.","Мин.","°CWB","-21","-21","-21","-21","-21 (1)","-21","-15"]
["","","","Макс.","°CWB","18","18","18","18","18","18","18"]
["Уровень звукового давления","Охлаждение","","Уровень звукового давления-=-Охлаждение-=-Ном.-=-дБ(A)","дБA","46","46","47","48","48","48","47"]
["","Hагрев","","Уровень звукового давления-=-Hагрев-=-Ном.-=-дБ(A)","дБA","47","47","49","49","49","49","48"]
["Хладагент","Тип","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Заправка","","","кг","0.95","0.95","0.95","0.95","1.10","1.15","1.15"]
["","Заправка","","","tCO2Eq","0.65","0.65","0.65","0.65","0.75","0.78","0.78"]
["","ПГП","","","","675","675","675","675","675","675","675"]
["Подсоединение труб","Длина трубы","Макс.","НБ - ВБ","м","20","20","20","30","30","30","30"]
["Подсоединения труб","Дополнительная заправка хладагента","","","кг/м","0,02 (для длины труб свыше 10 м)","0,02 (для длины труб свыше 10 м)","0,02 (для длины труб свыше 10 м)","0,02 (для длины труб свыше 10 м)","0,02 (для длины труб свыше 10 м)","0,02 (для длины труб свыше 10 м)","0,02 (для длины труб свыше 10 м)"]
["","перепад уровня","IU - OU","Макс.","м","15","15","15","20","20","20","20"]
["Электропитание","Фаза","","","","1~","1~","1~","1~","1~","1~","1~"]
["","Частота","","","Гц","50","50","50","50","50","50","50"]
["","Напряжение","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Стандартные аксессуары","Installation manual","","","","1","1","1","1","1","1","1"]
["","Drain joint","","","","1","1","1","1","1"]
["","Refrigerant charge label","","","","1","1","1","1","1","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1","1","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1","1","1"]
["","Drain cap","","","","3","3","3","3","1","3","3"]
["Примечания","","","","","","","","","(1) - Рабочий диапазон см. в отдельных чертежах","(1) - Рабочий диапазон см. в отдельных чертежах","(1) - Рабочий диапазон см. в отдельных чертежах"]
["","","","","","","","","","(2) - Электрические параметры см. в отдельных чертежах","(2) - Электрические параметры см. в отдельных чертежах","(2) - Электрические параметры см. в отдельных чертежах"]
["","","","","","","","","","(3) - Содержит фторированные парниковые газы","(3) - Содержит фторированные парниковые газы","(3) - Содержит фторированные парниковые газы"]
["Стандартные аксессуары","Drain plug","","","","","","","","","1","1"]